## Slide 1
February 2019

## Slide 2: Firefighters Lifts
February 2019

## Slide 3: Roger Howkins ASSOCIATE | Arup
3
Firefighters Lifts

## Slide 4
4
Firefighters Lifts
Firefighter lift - Description
A firefighters lift is a lift provided within
a tall building, complex building or
a building with deep basement.
The purpose of a firefighters lift is
to provide a facility to assist firefighters
to move with more ease vertically
through a building.

## Slide 5: Firefighters Lifts BS EN 81-72:2015
5
Firefighters Lifts

## Slide 6
6
Firefighters Lifts
Definitions
Firefighter lift:
lift with protection measures, controls and signals that enable it to be used under the direct control of the fire and rescue service in fighting a fire
Fire-fighting Shaft:
protected enclosure containing a fire-fighting stair, fire-fighting lobbies, a fire main and, if provided, a firefighters lift together with any machinery space
Lift well:
space, usually bounded by the bottom of the pit, the walls and the ceiling of the well, in which the lift car, the counterweight or the balancing weight travels
Fire and rescue service access level (FSAL):
level at which fire and rescue service vehicles have access and from which there is suitable entry to a building

## Slide 7
7
Firefighters Lifts
BS EN 81-72:2015
It does not cover:
Lifts in partially enclosed wells for use as firefighters lifts
Lifts installed in new/existing building not in a fire resisting structure
Important modification to existing lifts

## Slide 8
8
Firefighters Lifts
BS EN 81-72:2015
It does not define:
Number of firefighters lifts and floors to be served
Size of the safe areas
The use of other than the highest deck of a multi deck lift for firefighting operations

## Slide 9
9
Firefighters Lifts
BS EN 81-72:2015
The following significant subjects are not dealt with:
Not having sufficient or correctly located firefighters lifts
Fire in lift well, safe area, machinery space or car
Building floor identification
Water management not working correctly

## Slide 10
10
Firefighters Lifts
Responsibility
It is responsibility of National Regulations to determine the require level of fire resistance
Firefighters lift cars should be clearly and conspicuously marked with a notice conforming to BS ISO 3864-1 stating:
“Firefighters lift: Do not use for goods or refuse”
NOTE
The “Do not use for goods or refuse” sign is a building sign and not part of the lift as defined in BS EN 81-72
(BS 9999:2017)
Fire door notice

## Slide 11
11
Firefighters Lifts
Fundamental of firefighters lifts
Must conform with BS EN 81-20:2014
Minimum car size of 1100mm wide by 1400mm deep (630kg/8-person)
Minimum door width of 800mm
For evacuation of a stretcher, minimum car size of 1100mm wide by 2100mm deep (1000kg/13-person)
Must be able to reach highest served level within 60 seconds (additional rules for travel over 200m)
Designed to operate during firefighting conditions for a period equal to structure

## Slide 12
12
Firefighters Lifts
  630kg/8-person
  1000kg/13-person
  (long car)
  for evacuation
  of a stretcher

## Slide 13
13
Firefighters Lifts
Fundamental of firefighters lifts
Electrical/electronic equipment on landings other than FSAL to operate correctly from 0° to 65°C
All other electrical/electronic equipment to operate correctly from 0° to 40°C
Shall operate in smoke filled wells and machinery spaces
Ambient temperature sensors shall not stop or prevent the start of a firefighters lift
No sprinklers within the wells or machinery spaces
Distance between consecutive landing entrances shall not exceed 7m
Consideration to be given to ladder length

## Slide 14
14
Firefighters Lifts
Protection of electrical equipment
Protection from dripping water in lift well within 1m
Equipment in lift pit (floor):
- less than 1m from pit floor to IP67
- socket outlets to be at least 0.5m above
permissible water level
Lift car roof:
- prevent accumulation of water,
drain required
- classification IPX3

## Slide 15
15
Firefighters Lifts
Rescue of trapped firefighters
630kg/8-person lift: trap door of 0.4m x 0.5m (clear dimensions)
1000kg/13-person lift: trap door of 0.5m x 0.7m (clear dimensions)
Ladders shall not rest against landing doors and shall be supported by suitable point on car roof

## Slide 16
16
Firefighters Lifts
Rescue
From outside of the car
Self rescue from inside the car
Rope ladders not permitted
Self rescue from inside the car
Rescue from outside of the car

## Slide 17
17
Firefighters Lifts CPD
Firefighting control system
Firefighting switch location:
Within 2m horizontal from lift
Height between 1.4m and 2m above floor level
Marked with firefighting pictogram
Marked with clear visual indication of which the switch is in firefighting operation
Firefighting pictogram

## Slide 18
18
Firefighters Lifts
Phase 1: priority recall
Switching onto firefighting control
The well and machinery spaces shall automatically illuminate
All car/landing calls shall be canceled
Door open and alarm buttons to remain operational
Fire service communication to be active
An audible signal on car and machinery spaces shall be initiated if lift is on maintenance

## Slide 19
19
Firefighters Lifts
Phase 2: use of lift under firefighting control
Not possible to register more than one car call
Constant pressure for call and door close button
Car call to be visually displayed on the car control panel

## Slide 20
20
Firefighters Lifts
Single entry car
  630kg/8-person
  1000kg/13-person
  (long car)
  for evacuation
  of a stretcher

## Slide 21
21
Firefighters Lifts CPD
Dual entry car
Only one car door shall open at a time
Only one car control panel to be in operation for firefighters lift
  1000kg/13-person (long car)
  for evacuation of a stretcher
  630kg/8-person

## Slide 22
22
Firefighters Lifts
Power supplies for firefighters lifts
Primary + secondary power supplies
Fire protection to be as lift well
Secondary power supply to run lift at rated speed and load
Secondary power to be sufficient for a period equal to the structure
Indication should be provided to show lift is on secondary supply
Changeover/interruption of electrical supply
To be established within 1 minute
Lift not to move more than one floor and towards the FSAL

## Slide 23
23
Firefighters Lifts
Firefighting lift equipment
Car
Operating Panel
(COP)
FSAL
Landing
Operating Panel
(LOP)
FSAL Landing Firefighting panel and intercom
Landing Firefighting intercom
Automatically operated horizontal sliding car and landing doors
Trap door

## Slide 24
24
Firefighters Lifts
Water management
Measures to address the ingress of water into well:
Drainage channels in front of every lift landing entrance
Raising or ramping of the floor in front of every lift landing entrance

## Slide 25
25
Firefighters Lifts
Water management
Measures to address the accumulation of water in the lift pit:
Drainage solutions should avoid having pumps or other non-lift equipment in the lift well
Drains to prevent water in the lift pit from reaching 1m level
Permanently installed drainage pumps to remove water from the lift pit, to be located outside the lift well, to be connected to the secondary power supply

## Slide 26
26
Firefighters Lifts
Testing
BS 8486-8:2018
Examination and test of new lifts before putting into service

## Slide 27
27
Firefighters Lifts
Maintenance requirements for firefighters lifts
Operation of firefighting switch | Weekly
Simulation of failure of primary power supply | Monthly
If secondary power is from a generator, it shall run for at least 1 hour | Annually
Full test of firefighting operation | Annually
Check for building issues, i.e. pumps | No time scale given
Lift contractor to make test of lifts and communication systems | Annually
Advise on any change of standards for operation in event of fire | -
These are in addition to normal routine lift maintenance:

## Slide 28: Thank you for your attention. QUESTIONS?